**AmaDrainer-Box Mini**

Reliable and compact grey water lifting unit in a modern design with activated carbon filter meeting hygiene requirements and with shower connection as standard, for floor mounting (or optionally for wall mounting).

Comprising: stable plastic collecting tank made of PP, pressure-sealed and odour-proof.

**Function:**

Automatic grey water lifting unit for collecting unpressurised, domestic waste water without faeces as well as stormwater and lifting it above the flood level.

**Features:**

AmaDrainer-Box Mini

- Activated carbon filter with overflow protection

- AmaDrainer 301 or AmaDrainer 301 C submersible motor pump, with integrated swing check valve, for automatic operation, with 3 m power cable and shockproof plug

**Operating data:**

Fluid handled:

Flow rate Q:

Head H:

Permissible fluid temperature: <= 50 °C in continuous operation

Free passage: 10 mm

**Drive:**

Operating voltage: 1-phase 230 V

Frequency 50 Hz

Rated power requirement P1: 0.43 kW

Motor rating P2: 0.25 kW

Nominal current: 1.9 A

Integrated temperature switch

**Monitoring / open-loop control / closed-loop control:**

Pump controlled via integrated float switch

**Materials:**

Tank: ABS

Pump: See description of the AmaDrainer 3 submersible motor pump

**Dimensions and connections:**

Collecting tank volume: 17 l

Discharge side: pipe DN 40 (spigot and socket connection), for connection on either the left or right hand side

Inlet side: vertical/horizontal: DN 32, DN 40 or DN 50 (spigot and socket connection) / shower connection: DN 50

Length: 328 mm

Width: 460 mm

Height: 321 mm

**Purchase order information:**

Make: KSB

Type series / size: AmaDrainer-Box Mini

Material pricing group: MW

Weight: 9 kg

**Material number:**

**Typical tender for AmaDrainer-Box**

**2336.522/02-EN**

**Subject to technical modification without prior notice.**

**25 August 2021**