***BOA-Compact:***

***Short text:***

Soft-seated globe valve with flanged ends, single-piece body made of EN-GJL-250, face-to-face length to EN 558/14, with handwheel, throttling plug, position indicator, locking device, travel stop and insulating cap with anti-condensation feature

**Manufacturer/type:** **KSB/BOA-Compact**

Pressure class: PN 6 or 16

Nominal size: DN 15-200

***Long text:***

Soft-seated globe valve with flanged ends,

single-piece body made of EN-GJL-250, face-to-face length to EN 558/14, straight-way valve in slanted seat design, with handwheel, throttling plug, position indicator, locking device, protected internal travel stop and insulating cap with anti-condensation feature; compact, fully EPDM-encapsulated throttling plug providing soft main and back seat; stem sealed by EPDM profile ring, maintenance-free, -10 to 120 °C; suitable for full insulation in acc. with German heating system regulations (HeizAnlV); non-rotating stem made of 1.4021 with protected, external thread, non-rising handwheel; with blue exterior coating (similar to RAL 5002); designed, manufactured, tested and marked in acc. with the European Pressure Equipment Directive.

**Manufacturer/type:** **KSB/BOA-Compact**

Pressure class: PN 6 or 16

Nominal size: DN 15-200

***Variants:***

with lead-sealable cap (prevents unauthorised actuation) as assembly set

or

with electric actuator

**Typical tender for BOA-Compact**

**7112.521/01-EN  
Subject to technical modification without prior notice**

**23 April 2018**